## Motor
Item | Value
Rating | 15 kW, 415 V, 50 Hz, 4-pole
Equivalent circuit | Rs 0.25 Ohm, Rr 0.2 Ohm, Lls = Llr 2.2 mH, Lm 70 mH, Rc 574 Ohm
Rated point | 97.4 N m, 1469 rpm, 26.1 A, pf 0.865, efficiency 92.4 %
Locked rotor at 415 V | 167 A (6.4 x rated)
Fan operating point | 13.5 kW at 1473 rpm, 23.9 A
Inertia (motor + impeller) | 1.5 kg m2

## Starting
Quantity | Value
DOL peak instantaneous current (A) | 253.27
DOL max 1-cycle rms current (A) | 173.62
DOL inrush / rated | 6.65
DOL first-cycle peak / rated rms | 9.71
DOL peak torque (N m) | 401.77
DOL time to 98 % speed (s) | 1.55
V/f max rms current (A) | 28.48
V/f max current / rated | 1.09
V/f peak torque (N m) | 110.19
V/f time to 98 % speed (s) | 9.85

## PWM
Item | Value
Operating point | 40 Hz, 334 V (V/f), 80 % fan speed
Carrier / DC bus | 3.96 kHz (mf = 99) / 560 V
Fundamental line voltage | 332.7 V rms
Fundamental current | 16.82 A rms
Current THD (to 20 kHz) | 4.24 %
Line voltage THD (to 20 kHz) | 63.3 %

## Energy summary
Application | kWh/year DOL | kWh/year V/f drive | Saving (kWh) | Saving (%) | Saving (INR at 8/kWh)
Fan with outlet damper | 79117 | 47132 | 31985 | 40.4 | 255876
Pump with throttling valve, 40 % static head | 79117 | 57140 | 21977 | 27.8 | 175819

## Energy by flow
Application | flow_pct | hours | shaft_kw_throttled | input_kw_dol | speed_pct | drive_hz | shaft_kw_vfd | motor_eff_vfd | input_kw_vfd
Fan with outlet damper | 100 | 600 | 13.5 | 14.59 | 100 | 50 | 13.5 | 0.93 | 14.96
Fan with outlet damper | 90 | 1200 | 12.86 | 13.89 | 90 | 44.91 | 9.84 | 0.92 | 10.98
Fan with outlet damper | 80 | 1800 | 12.26 | 13.25 | 80 | 39.84 | 6.91 | 0.92 | 7.78
Fan with outlet damper | 70 | 1500 | 11.71 | 12.65 | 70 | 34.79 | 4.63 | 0.91 | 5.28
Fan with outlet damper | 60 | 900 | 11.19 | 12.09 | 60 | 29.76 | 2.92 | 0.89 | 3.4
Pump with throttling valve, 40 % static head | 100 | 600 | 13.5 | 14.59 | 100 | 50 | 13.5 | 0.93 | 14.96
Pump with throttling valve, 40 % static head | 90 | 1200 | 12.86 | 13.89 | 93.32 | 46.58 | 10.78 | 0.92 | 12
Pump with throttling valve, 40 % static head | 80 | 1800 | 12.26 | 13.25 | 86.9 | 43.31 | 8.52 | 0.92 | 9.54
Pump with throttling valve, 40 % static head | 70 | 1500 | 11.71 | 12.65 | 80.82 | 40.22 | 6.68 | 0.92 | 7.52
Pump with throttling valve, 40 % static head | 60 | 900 | 11.19 | 12.09 | 75.15 | 37.34 | 5.2 | 0.91 | 5.91